## Basic Par.-Nroom100-Tab.1, 2
- Basic technical parameters - Nroom-100 (NR1-010-ECxxHR...) - Tab.1
| Line |  |  | NR1-010-ECS0HRX… | NR1-010-ECV1HRX… | NR1-010-ECE1HRX… | NR1-010-ECS0HRP… | NR1-010-ECV1HRP… | NR1-010-ECE1HRP…
| Type of recovery exchanger |  |  | HRV with temperature efficiency
| Unit equipment | pre-heater |  | - | - | - | electric | electric | electric
|  | after heater |  | - | water | electric | - | water | electric
| Nominal airflow/ BOOST* |  | m3/h | 100/250
| Heat output (range) of heating** |  | kW | - | 0.33 - 1.38 | 0.5 | - | 0.33 - 1.38 | 0.5
| Noise level** |  | dB(A) | 32.1
| Weight**** |  | kg | 16.3 | 18.3 | 19.3 | 16.8 | 18.8 | 19.8
| Water volume in exchanger |  | l | - | 0.51 | - | - | 0.51 | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of the unit / BOOST* |  | W | 30/167 | 30/167 | 530/667 | 300/437 | 300/437 | 800/937
| Nominal current of the unit / BOOST* |  | A | 0.3/1.32 | 0.3/1.32 | 2.5/3.5 | 1.5/2.5 | 1.5/2.5 | 3.7/4.7
| Recovery efficiency per EN 308 | heat | % | up to 94
|  | humidity | % | - | - | - | - | - | -
| Protection type |  | IP | 20
| Energy efficiency class (ERP) |  |  | cold climate A+, medium climate A, warm climate A
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging
- Basic technical parameters - Nroom-100 (NR1-01-ECxxER...) - Tab. 2
| Line |  |  | NR1-010-ECS0ERX… | NR1-010-ECV1ERX… | NR1-010-ECE1ERX… | NR1-010-ECS0ERP… | NR1-010-ECV1ERP… | NR1-010-ECE1ERP…
| Type of recovery exchanger |  |  | ERV with temperature and humidity efficiency
| Unit equipment | pre-heater |  | - | - | - | electric | electric | electric
|  | after heater |  | - | water | electric | - | water | electric
| Nominal airflow/ BOOST* |  | m3/h | 90/205
| Heat output (range) of heating** |  | kW | - | 0.29 - 1.24 | 0.5 | - | 0.29 - 1.24 | 0.5
| Noise level** |  | dB(A) | 32.1
| Weight**** |  | kg | 16.3 | 18.3 | 19.3 | 16.8 | 18.8 | 19.8
| Water volume in exchanger |  | l | - | 0.51 | - | - | 0.51 | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of the unit / BOOST* |  | W | 30/167 | 30/167 | 530/667 | 300/437 | 300/437 | 800/937
| Nominal current of the unit / BOOST* |  | A | 0.3/1.32 | 0.3/1.32 | 2.5/3.5 | 1.5/2.5 | 1.5/2.5 | 3.7/4.7
| Recovery efficiency per EN 308 | heat | % | up to 90
|  | humidity | % | up to 85
| Protection type |  | IP | 20
| Energy efficiency class (ERP) |  |  | cold climate A+, medium climate A, warm climate B
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging

## Basic Par.-Nroom250-Tab.3, 4
- Basic technical parameters - Nroom-250 (NR1-025-ECxxHR...) - Tab 3
| Line |  |  | NR1-025-ECS0HRX… | NR1-025-ECV1HRX… | NR1-025-ECE1HRX… | NR1-025-ECS0HRP… | NR1-025-ECV1HRP… | NR1-025-ECE1HRP…
| Type of recovery exchanger |  |  | HRV with temperature efficiency
| Unit equipment | pre-heater |  | - | - | - | electric | electric | electric
|  | after heater |  | - | water | electric | - | water | electric
| Nominal airflow/ BOOST* |  | m3/h | 250/350
| Heat output (range) of heating** |  | kW | - | 1.34 - 3.49 | 1 | - | 1.34 - 3.49 | 1
| Noise level** |  | dB(A) | 32.6
| Weight**** |  | kg | 36 | 39.4 | 41.2 | 37 | 40.4 | 42.2
| Water volume in exchanger |  | l | - | 1.17 | - | - | 1.17 | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of the unit / BOOST* |  | W | 61/169 | 61/169 | 1061/1169 | 479/709 | 480/709 | 1480/1709
| Nominal current of the unit / BOOST* |  | A | 0.61/1.42 | 0.61/1.42 | 5/5.8 | 3/3.8 | 3/3.8 | 7.3/8.2
| Recovery efficiency per EN 308 | heat | % | up to 94
|  | humidity | % | - | - | - | - | - | -
| Protection type |  | IP | 20
| Energy efficiency class (ERP) |  |  | cold climate A+, medium climate A, warm climate B
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging
- Basic technical parameters - Nroom-250 (NR1-025-ECxxER...) - Tab. 4
| Line |  |  | NR1-025-ECS0ERX… | NR1-025-ECV1ERX… | NR1-025-ECE1ERX… | NR1-025-ECS0ERP… | NR1-025-ECV1ERP… | NR1-025-ECE1ERP…
| Type of recovery exchanger |  |  | ERV with temperature and humidity efficiency
| Unit equipment | pre-heater |  | - | - | - | electric | electric | electric
|  | after heater |  | - | water | electric | - | water | electric
| Nominal airflow/ BOOST* |  | m3/h | 240/335
| Heat output (range) of heating** |  | kW | - | 1.34 - 3.49 | 1 | - | 1.34 - 3.49 | 1
| Noise level** |  | dB(A) | 32.6
| Weight**** |  | kg | 36 | 39.4 | 41.2 | 37 | 40.4 | 42.2
| Water volume in exchanger |  | l | - | 1.17 | - | - | 1.17 | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of the unit / BOOST* |  | W | 61/169 | 61/169 | 1061/1169 | 479/709 | 480/709 | 1480/1709
| Nominal current of the unit / BOOST* |  | A | 0.61/1.42 | 0.61/1.42 | 5/5.8 | 3/3.8 | 3/3.8 | 7.3/8.2
| Recovery efficiency per EN 308 | heat | % | up to 86
|  | humidity | % | up to 75
| Protection type |  | IP | 20
| Energy efficiency class (ERP) |  |  | cold climate A+, medium climate A, warm climate B
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging

## Packaging
Line | box | Name | Weight |  | package size * | number of units on a pallet - max. stackability
|  |  | Gross | Net
|  |  | kg | kg | m | pc
Nroom-100 | Nroom unit | NR1-010-ECS0HRX… | 19.2 | 16.3 | 1.05 x 0.7 x 0.31 | 5
|  | NR1-010-ECV1HRX… | 21.2 | 18.3
|  | NR1-010-ECE1HRX… | 22.2 | 19.3
|  | NR1-010-ECS0HRP… | 19.7 | 16.8
|  | NR1-010-ECV1HRP… | 21.7 | 18.8
|  | NR1-010-ECE1HRP… | 22.7 | 19.8
| Mandatory accessories | NR1-010-DUCT-1 | 1.4 | 1.2 | 0.6 x 0.4 x 0.21 | 40
Nroom-250 | Nroom unit | NR1-025-ECS0HRX… | 41.1 | 36 | 1.6 x 0.84 x 0.36 | 5
|  | NR1-025-ECV1HRX… | 44.5 | 39.4
|  | NR1-025-ECE1HRX… | 46.3 | 41.2
|  | NR1-025-ECS0HRP… | 42.1 | 37
|  | NR1-025-ECV1HRP… | 45.5 | 40.4
|  | NR1-025-ECE1HRP… | 47.3 | 42.2
| Mandatory accessories | NR1-025-DUCT-1 | 1.9 | 1.7 | 0.6 x 0.4 x 0.21 | 40
* package dimensions are indicated in the width x length x height order

## noise - Tab. 5, 6, 7, 8
- NR1-010-EC... - interior (indoor) radiation of the unit - Tab. 5
Degree of air output | [7 empty] | Sound Power Level LWA [dB(A)] | Sound pressure level in the open field on the reflection plane
| 125 | 250 | 500 | 1 | 2 | 4 | 8 |  | LPA [dB] in 1 m | LPA [dB] in 3 m
1.- min/heating mode | 21.5022 | 25.9466 | 29.7232 | 27.6308 | 21.002 | 18.7136 | 17.5356 | 33.6546 | 19.8 | 12.1
4. | 28.7709 | 43.421 | 41.2898 | 39.3725 | 34.3194 | 24.3061 | 18.0051 | 47.0236 | 33.12 | 25.52
7.- nominal flow | 32.0489 | 49.0806 | 48.6771 | 46.8764 | 42.994 | 33.1825 | 23.0732 | 53.5651 | 39.7 | 32.1
Boost* | 41.9799 | 56.9094 | 67.1176 | 62.4096 | 59.5012 | 51.9129 | 45.1689 | 69.2833 | 55.4 | 47.8
* BOOST mode - intensive ventilation
- NR1-010-EC... - exterior radiation of the unit (outdoor inlet, exhaust) - Tab. 6
Degree of air output | [7 empty] | Sound power level LWA [dB (A)] | Sound pressure level in the open field on the reflection plane
| 125 | 250 | 500 | 1 | 2 | 4 | 8 |  | LPA [dB] in 1 m | LPA [dB] in 3 m
1.- min/heating mode | 34.6866 | 32.0893 | 35.7823 | 32.1834 | 21.9819 | 22.2764 | 24.6999 | 37.3206 | 23.6902 | 14.5879
4. | 46.4121 | 53.7006 | 49.7068 | 45.8597 | 35.9206 | 28.9337 | 25.3612 | 52.1459 | 39.6272 | 30.7671
7.- nominal flow | 51.7 | 60.7 | 58.6 | 54.6 | 45 | 39.5 | 32.5 | 59.4 | 47.5 | 38.7
Boost* | 67.7204 | 70.3822 | 80.7995 | 72.6926 | 62.2774 | 61.7964 | 63.6231 | 76.8305 | 66.2846 | 57.628
* BOOST mode - intensive ventilation
- NR1-025-EC... - interior (indoor) radiation of the unit - Tab. 7.
Degree of air output | [7 empty] | Sound power level LWA [dB (A)] | Sound pressure level in the open field on the reflection plane
| 125 | 250 | 500 | 1 | 2 | 4 | 8 |  | LPA [dB] in 1 m | LPA [dB] in 3 m
1.- min/heating mode | 18.5853 | 29.522 | 28.9093 | 25.6908 | 22.2448 | 15.8486 | 13.2816 | 34.3783 | 20.0697 | 12.7272
4. | 23.4862 | 42.5587 | 42.0107 | 37.6051 | 33.8094 | 21.8628 | 13.2488 | 46.2633 | 31.9288 | 24.5472
7.- nominal flow | 27.9399 | 48.8452 | 50.8905 | 46.1852 | 43.2188 | 33.0928 | 19.6789 | 54.2169 | 39.8 | 32.6001
Boost* | 37.6295 | 56.6457 | 62.8941 | 59.5747 | 56.8095 | 47.6947 | 36.7572 | 65.8984 | 51.4985 | 44.1944
* BOOST mode - intensive ventilation
- NR1-025-EC... - exterior radiation of the unit (outdoor inlet, exhaust) - Tab. 8
Degree of air output | [7 empty] | Sound power level LWA [dB (A)] | Sound pressure level in the open field on the reflection plane
| 125 | 250 | 500 | 1 | 2 | 4 | 8 |  | LPA [dB] in 1 m | LPA [dB] in 3 m
1.- min/heating mode | 29.9811 | 36.5111 | 34.8025 | 29.9237 | 23.2827 | 18.866 | 18.708 | 38.1232 | 24.0128 | 15.344
4. | 37.887 | 52.6341 | 50.5746 | 43.8011 | 35.3868 | 26.0252 | 18.6617 | 51.3028 | 38.202 | 29.5943
7.- nominal flow | 45.0716 | 60.4089 | 61.2646 | 53.7949 | 45.2353 | 39.3932 | 27.7189 | 60.1228 | 47.6196 | 39.3029
Boost* | 60.7025 | 70.0561 | 75.7151 | 69.3906 | 59.4601 | 56.7751 | 51.7747 | 73.0768 | 61.6166 | 53.2811
* BOOST mode - intensive ventilation

## Soundproofing - Tab. 9
- sound permeability from the exterior
Line | Nroom-100 |  | Nroom-250
Degree of air output | Evaluated acoustic attenuation | Evaluated difference of the standard level | Evaluated acoustic attenuation | Evaluated difference of the standard level
| RW,P (C,Ctr) [dB] | Dn, e, w (C,Ctr) [dB] | RW,P (C,Ctr) [dB] | Dn, e, w (C,Ctr) [dB]
Standby | 17 (-1; -3) | 42 (-2; -3) | 17 (-1; -3) | 42 (-2; -3)
7.- nominal flow | 17 (-1; -3) | 42 (-1; -2) | 17 (-1; -3) | 42 (-1; -2)

## water - Nroom100 - Tab.10, 11
Technical data of water heaters
- NR1-010-ECV1HR… (heat recovery exchanger) - Tab. 10
Temperature gradient |  |  | 80/60 |  |  |  | 75/65 |  |  |  | 75/60 |  |  |  | 70/60 |  |  |  | 70/50
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 28 | 0.47 | 75.3 | 0.02 | 0.2 | 0.42 | 72.9 | 0.03 | 0.4 | 0.42 | 71.6 | 0.03 | 0.4 | 0.39 | 67.8 | 0.04 | 0.6 | 0.37 | 64.1 | 0.01 | 0.2
| 4. | 66 | 1.25 | 65.7 | 0.06 | 1 | 1.26 | 64.7 | 0.11 | 3.2 | 1.22 | 63 | 0.07 | 1.5 | 1.15 | 60.2 | 0.1 | 2.8 | 1.07 | 56.3 | 0.05 | 0.7
| 7.- nominal flow | 100 | 1.78 | 60.6 | 0.08 | 1.7 | 1.76 | 60.1 | 0.16 | 5.8 | 1.7 | 58.3 | 0.1 | 2.7 | 1.62 | 56 | 0.14 | 5.1 | 1.48 | 52 | 0.06 | 1.3
15 | 1.- min/heating mode | 28 | 0.4 | 74.9 | 0.01 | 0.2 | 0.38 | 72.9 | 0.04 | 0.6 | 0.38 | 71.7 | 0.02 | 0.3 | 0.34 | 67.9 | 0.03 | 0.6 | 0.33 | 64.2 | 0.02 | 0.2
| 4. | 66 | 1.16 | 66.5 | 0.05 | 0.8 | 1.14 | 65.5 | 0.1 | 2.7 | 1.1 | 63.7 | 0.06 | 1.3 | 1.04 | 60.9 | 0.09 | 2.3 | 0.95 | 56.8 | 0.04 | 0.6
| 7.- nominal flow | 100 | 1.62 | 61.7 | 0.07 | 1.2 | 1.6 | 61.3 | 0.14 | 4.9 | 1.54 | 59.4 | 0.09 | 2.3 | 1.41 | 57.1 | 0.13 | 4.2 | 1.32 | 53 | 0.06 | 1.1
20 | 1.- min/heating mode | 28 | 0.35 | 74.9 | 0.01 | 0.2 | 0.35 | 73 | 0.03 | 0.5 | 0.33 | 71.5 | 0.02 | 0.2 | 0.31 | 67.9 | 0.02 | 0.5 | 0.29 | 64.2 | 0.01 | 0.1
| 4. | 66 | 1.05 | 67.1 | 0.05 | 0.7 | 1.03 | 66.2 | 0.09 | 2.3 | 0.99 | 64.5 | 0.06 | 1 | 0.93 | 61.7 | 0.08 | 1.9 | 0.83 | 57.2 | 0.04 | 0.5
| 7.- nominal flow | 100 | 1.46 | 62.7 | 0.06 | 1.2 | 1.44 | 62.4 | 0.13 | 4.1 | 1.38 | 60.5 | 0.08 | 1.9 | 1.3 | 58.1 | 0.11 | 3.5 | 1.16 | 53.9 | 0.05 | 0.8
- connection dimension male thread 3/4"
- NR1-010-ECV1HR… (heat recovery exchanger) - continued Tab. 10
Temperature gradient |  |  | 65/50 |  |  |  | 55/45 |  |  |  | 45/35 |  |  |  | 40/30
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 28 | 0.35 | 60.9 | 0.02 | 0.3 | 0.28 | 52.4 | 0.03 | 0.4 | 0.21 | 41.9 | 0.03 | 0.2 | 0.18 | 36.8 | 0.02 | 0.1
| 4. | 66 | 0.68 | 57.4 | 0.04 | 0.6 | 0.56 | 49.5 | 0.05 | 0.8 | 0.42 | 39.6 | 0.04 | 0.5 | 0.35 | 34.6 | 0.03 | 0.3
| 7.- nominal flow | 100 | 1.4 | 49.8 | 0.08 | 2 | 1.17 | 43.4 | 0.1 | 3.1 | 0.88 | 34.9 | 0.08 | 1.9 | 0.72 | 30.4 | 0.06 | 1.4
15 | 1.- min/heating mode | 28 | 0.31 | 60.9 | 0.03 | 0.2 | 0.25 | 52.3 | 0.02 | 0.3 | 0.19 | 41.9 | 0.02 | 0.1 | 0.15 | 36.9 | 0.01 | 0.1
| 4. | 66 | 0.6 | 57.7 | 0.04 | 0.4 | 0.49 | 49.8 | 0.04 | 0.7 | 0.35 | 39.8 | 0.03 | 0.3 | 0.28 | 34.9 | 0.02 | 0.2
| 7.- nominal flow | 100 | 1.24 | 50.9 | 0.07 | 1.6 | 1.02 | 44.4 | 0.09 | 2.4 | 0.72 | 35.8 | 0.06 | 1.3 | 0.56 | 31.1 | 0.05 | 0.9
20 | 1.- min/heating mode | 28 | 0.26 | 60.8 | 0.01 | 0.2 | 0.2 | 52.1 | 0.03 | 0.2 | 0.16 | 42.1 | 0.01 | 0.1 | 0.12 | 36.9 | 0.01 | 0.1
| 4. | 66 | 0.52 | 57.9 | 0.03 | 0.4 | 0.41 | 50 | 0.04 | 0.5 | 0.28 | 40.1 | 0.02 | 0.2 | 0.21 | 35.1 | 0.02 | 0.2
| 7.- nominal flow | 100 | 1.09 | 51.8 | 0.06 | 1.3 | 0.86 | 45.4 | 0.08 | 1.8 | 0.56 | 36.4 | 0.05 | 0.9 | 0.4 | 31.8 | 0.03 | 0.3
- connection dimension male thread 3/4"
- NR1-010-ECV1ER… (enthalpy recovery exchanger) - Tab.11
Temperature gradient |  |  | 80/60 |  |  |  | 75/65 |  |  |  | 75/60 |  |  |  | 70/60 |  |  |  | 70/50
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 28 | 0.423 | 67.77 | 0.018 | 0.2 | 0.378 | 65.61 | 0.027 | 0.5 | 0.378 | 64.44 | 0.027 | 0.3 | 0.351 | 61.02 | 0.036 | 0.6 | 0.333 | 57.69 | 0.009 | 0.2
| 4. | 66 | 1.125 | 59.13 | 0.054 | 0.9 | 1.134 | 58.23 | 0.099 | 2.88 | 1.098 | 56.7 | 0.063 | 1.35 | 1.035 | 54.18 | 0.09 | 2.52 | 0.963 | 50.67 | 0.045 | 0.63
| 7.- nominal flow | 100 | 1.602 | 54.54 | 0.072 | 1.53 | 1.584 | 54.09 | 0.144 | 5.22 | 1.53 | 52.47 | 0.09 | 2.43 | 1.458 | 50.4 | 0.126 | 4.59 | 1.332 | 46.8 | 0.054 | 1.17
15 | 1.- min/heating mode | 28 | 0.36 | 67.41 | 0.009 | 0.2 | 0.342 | 65.61 | 0.036 | 0.6 | 0.342 | 64.53 | 0.018 | 0.2 | 0.306 | 61.11 | 0.027 | 0.5 | 0.297 | 57.78 | 0.018 | 0.1
| 4. | 66 | 1.044 | 59.85 | 0.045 | 0.72 | 1.026 | 58.95 | 0.09 | 2.43 | 0.99 | 57.33 | 0.054 | 1.17 | 0.936 | 54.81 | 0.081 | 2.07 | 0.855 | 51.12 | 0.036 | 0.54
| 7.- nominal flow | 100 | 1.458 | 55.53 | 0.063 | 1.08 | 1.44 | 55.17 | 0.126 | 4.41 | 1.386 | 53.46 | 0.081 | 2.07 | 1.269 | 51.39 | 0.117 | 3.78 | 1.188 | 47.7 | 0.054 | 0.99
20 | 1.- min/heating mode | 28 | 0.315 | 67.41 | 0.009 | 0.1 | 0.315 | 65.7 | 0.027 | 0.5 | 0.297 | 64.35 | 0.018 | 0.2 | 0.279 | 61.11 | 0.018 | 0.4 | 0.261 | 57.78 | 0.01 | 0.1
| 4. | 66 | 0.945 | 60.39 | 0.045 | 0.63 | 0.927 | 59.58 | 0.081 | 2.07 | 0.891 | 58.05 | 0.054 | 0.9 | 0.837 | 55.53 | 0.072 | 1.71 | 0.747 | 51.48 | 0.036 | 0.45
| 7.- nominal flow | 100 | 1.314 | 56.43 | 0.054 | 1.08 | 1.296 | 56.16 | 0.117 | 3.69 | 1.242 | 54.45 | 0.072 | 1.71 | 1.17 | 52.29 | 0.099 | 3.15 | 1.044 | 48.51 | 0.045 | 0.72
- connection dimension male thread 3/4"
- NR1-010-ECV1ER… (enthalpy recovery ) - continued Tab.11
Temperature gradient |  |  | 65/50 |  |  |  | 55/45 |  |  |  | 45/35 |  |  |  | 40/30
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 28 | 0.315 | 54.81 | 0.018 | 0.2 | 0.252 | 47.16 | 0.027 | 0.3 | 0.189 | 37.71 | 0.027 | 0.2 | 0.162 | 33.12 | 0.018 | 0.1
| 4. | 66 | 0.909 | 48.51 | 0.054 | 0.99 | 0.756 | 41.94 | 0.063 | 1.53 | 0.567 | 33.57 | 0.045 | 0.99 | 0.468 | 29.16 | 0.036 | 0.72
| 7.- nominal flow | 100 | 1.26 | 44.82 | 0.072 | 1.8 | 1.053 | 39.06 | 0.09 | 2.79 | 0.792 | 31.41 | 0.072 | 1.71 | 0.648 | 27.36 | 0.054 | 1.26
15 | 1.- min/heating mode | 28 | 0.279 | 54.81 | 0.027 | 0.2 | 0.225 | 47.07 | 0.018 | 0.3 | 0.171 | 37.71 | 0.018 | 0.1 | 0.135 | 33.21 | 0.01 | 0.1
| 4. | 66 | 0.801 | 49.05 | 0.045 | 0.81 | 0.657 | 42.57 | 0.054 | 1.17 | 0.459 | 33.93 | 0.036 | 0.63 | 0.369 | 29.61 | 0.036 | 0.45
| 7.- nominal flow | 100 | 1.116 | 45.81 | 0.063 | 1.44 | 0.918 | 39.96 | 0.081 | 2.16 | 0.648 | 32.22 | 0.054 | 1.17 | 0.504 | 27.99 | 0.045 | 0.81
20 | 1.- min/heating mode | 28 | 0.234 | 54.72 | 0.009 | 0.2 | 0.18 | 46.89 | 0.027 | 0.2 | 0.144 | 37.89 | 0.01 | 0.1 | 0.108 | 33.21 | 0.009 | 0.1
| 4. | 66 | 0.702 | 49.5 | 0.045 | 0.63 | 0.558 | 43.11 | 0.045 | 0.9 | 0.36 | 34.29 | 0.045 | 0.45 | 0.27 | 29.97 | 0.027 | 0.18
| 7.- nominal flow | 100 | 0.981 | 46.62 | 0.054 | 1.17 | 0.774 | 40.86 | 0.072 | 1.62 | 0.504 | 32.76 | 0.045 | 0.81 | 0.36 | 28.62 | 0.027 | 0.27
- connection dimension male thread 3/4"

## water - Nroom250 - Tab.12, 13
Technical data of water heaters
- NR1-025-ECV1HR... (heat recovery exchanger) -Table 12
Temperature gradient |  |  | 80/60 |  |  |  | 75/65 |  |  |  | 75/60 |  |  |  | 70/60 |  |  |  | 70/50
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 64 | 1.68 | 73.8 | 0.07 | 3.2 | 1.61 | 70.9 | 0.14 | 10 | 1.58 | 70 | 0.1 | 4.8 | 1.48 | 66.1 | 0.13 | 8.8 | 1.42 | 63.9 | 0.06 | 2.4
| 4. | 157 | 2.87 | 68.1 | 0.12 | 8.1 | 2.78 | 66.3 | 0.27 | 26.1 | 2.71 | 64.9 | 0.17 | 12.3 | 2.55 | 61.7 | 0.22 | 22.9 | 2.41 | 58.8 | 0.11 | 6.1
| 7.- nominal flow | 250 | 4.38 | 61.8 | 0.22 | 16.9 | 4.26 | 60.7 | 0.4 | 55.7 | 4.16 | 59.2 | 0.26 | 26 | 3.94 | 56.6 | 0.35 | 48.8 | 3.66 | 53.3 | 0.16 | 12.8
15 | 1.- min/heating mode | 64 | 1.56 | 73.9 | 0.06 | 2.8 | 1.48 | 71.1 | 0.12 | 8.7 | 1.46 | 70.1 | 0.09 | 4.2 | 1.36 | 66.3 | 0.12 | 7.6 | 1.3 | 64 | 0.06 | 2.1
| 4. | 157 | 2.65 | 68.6 | 0.11 | 7 | 2.57 | 66.8 | 0.23 | 22.7 | 2.5 | 65.5 | 0.15 | 10.7 | 2.34 | 62.3 | 0.21 | 19.6 | 2.19 | 59.2 | 0.1 | 5.2
| 7.- nominal flow | 250 | 4 | 62.7 | 0.2 | 14.7 | 3.96 | 61.7 | 0.37 | 48.5 | 3.83 | 60.1 | 0.23 | 22.5 | 3.61 | 57.5 | 0.32 | 41.8 | 3.32 | 54.1 | 0.15 | 10.8
20 | 1.- min/heating mode | 64 | 1.43 | 74.1 | 0.05 | 2.4 | 1.36 | 71.4 | 0.11 | 7.5 | 1.34 | 70.3 | 0.08 | 3.6 | 1.23 | 66.5 | 0.11 | 6.4 | 1.17 | 64 | 0.05 | 1.7
| 4. | 157 | 2.44 | 69.1 | 0.1 | 6.1 | 2.35 | 67.4 | 0.21 | 19.5 | 2.28 | 66 | 0.13 | 9.1 | 2.13 | 62.8 | 0.19 | 16.6 | 1.97 | 59.7 | 0.09 | 4.3
| 7.- nominal flow | 250 | 3.71 | 63.6 | 0.18 | 12.7 | 3.63 | 62.6 | 0.3 | 41.6 | 3.49 | 61.1 | 0.21 | 19.2 | 3.27 | 58.5 | 0.29 | 35.3 | 2.98 | 55 | 0.13 | 8.9
- connection dimension male thread 3/4"
- NR1-025-ECV1HR… (heat recovery exchanger) - Tab. 10
Temperature gradient |  |  | 65/50 |  |  |  | 55/45 |  |  |  | 45/35 |  |  |  | 40/30
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 64 | 1.32 | 60.2 | 0.08 | 3.6 | 0.85 | 51.9 | 0.07 | 3.5 | 0.84 | 41.7 | 0.07 | 3.5 | 0.7 | 36.7 | 0.06 | 2.7
| 4. | 157 | 2.26 | 55.7 | 0.13 | 9.2 | 1.44 | 49 | 0.13 | 8.8 | 1.42 | 38.9 | 0.12 | 9 | 1.2 | 34.2 | 0.1 | 6.7
| 7.- nominal flow | 250 | 3.45 | 50.8 | 0.2 | 19.4 | 2.2 | 45.9 | 0.19 | 18.5 | 2.17 | 35.7 | 0.19 | 18.8 | 1.81 | 31.5 | 0.16 | 14
15 | 1.- min/heating mode | 64 | 1.2 | 60.3 | 0.07 | 3 | 0.97 | 51.7 | 0.08 | 4.4 | 0.71 | 41.8 | 0.06 | 2.6 | 0.57 | 36.7 | 0.05 | 1.9
| 4. | 157 | 2 | 56.2 | 0.12 | 7.7 | 1.66 | 48.6 | 0.15 | 11.3 | 1.2 | 39.3 | 0.1 | 6.7 | 0.97 | 34.6 | 0.08 | 4.7
| 7.- nominal flow | 250 | 3.1 | 51.7 | 0.18 | 16.2 | 2.54 | 45 | 0.22 | 23.9 | 1.83 | 36.6 | 0.16 | 13.9 | 1.46 | 32.3 | 0.13 | 9.6
20 | 1.- min/heating mode | 64 | 1.07 | 60.5 | 0.06 | 2.5 | 1.1 | 51.5 | 0.1 | 5.5 | 0.58 | 41.8 | 0.05 | 1.9 | 0.44 | 36.5 | 0.04 | 1.2
| 4. | 157 | 1.82 | 56.7 | 0.11 | 6.3 | 1.88 | 48 | 0.16 | 14 | 0.98 | 39.7 | 0.09 | 4.7 | 0.74 | 34.8 | 0.06 | 2.9
| 7.- nominal flow | 250 | 2.77 | 52.6 | 0.16 | 13.2 | 2.88 | 44.1 | 0.25 | 29.7 | 1.48 | 37.4 | 0.13 | 9.6 | 1.11 | 33 | 0.1 | 5.9
- connection dimension male thread 3/4"
- NR1-025-ECV1ER... (enthalpy recovery exchanger) - Tab.13
Temperature gradient |  |  | 80/60 |  |  |  | 75/65 |  |  |  | 75/60 |  |  |  | 70/60 |  |  |  | 70/50
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 62 | 1.68 | 73.8 | 0.07 | 3.2 | 1.61 | 70.9 | 0.14 | 10 | 1.58 | 70 | 0.1 | 4.8 | 1.48 | 66.1 | 0.13 | 8.8 | 1.42 | 63.9 | 0.06 | 2.4
| 4. | 151 | 2.87 | 68.1 | 0.12 | 8.1 | 2.78 | 66.3 | 0.27 | 26.1 | 2.71 | 64.9 | 0.17 | 12.3 | 2.55 | 61.7 | 0.22 | 22.9 | 2.41 | 58.8 | 0.11 | 6.1
| 7.- nominal flow | 240 | 4.38 | 61.8 | 0.22 | 16.9 | 4.26 | 60.7 | 0.4 | 55.7 | 4.16 | 59.2 | 0.26 | 26 | 3.94 | 56.6 | 0.35 | 48.8 | 3.66 | 53.3 | 0.16 | 12.8
15 | 1.- min/heating mode | 62 | 1.56 | 73.9 | 0.06 | 2.8 | 1.48 | 71.1 | 0.12 | 8.7 | 1.46 | 70.1 | 0.09 | 4.2 | 1.36 | 66.3 | 0.12 | 7.6 | 1.3 | 64 | 0.06 | 2.1
| 4. | 151 | 2.65 | 68.6 | 0.11 | 7 | 2.57 | 66.8 | 0.23 | 22.7 | 2.5 | 65.5 | 0.15 | 10.7 | 2.34 | 62.3 | 0.21 | 19.6 | 2.19 | 59.2 | 0.1 | 5.2
| 7.- nominal flow | 240 | 4 | 62.7 | 0.2 | 14.7 | 3.96 | 61.7 | 0.37 | 48.5 | 3.83 | 60.1 | 0.23 | 22.5 | 3.61 | 57.5 | 0.32 | 41.8 | 3.32 | 54.1 | 0.15 | 10.8
20 | 1.- min/heating mode | 62 | 1.43 | 74.1 | 0.05 | 2.4 | 1.36 | 71.4 | 0.11 | 7.5 | 1.34 | 70.3 | 0.08 | 3.6 | 1.23 | 66.5 | 0.11 | 6.4 | 1.17 | 64 | 0.05 | 1.7
| 4. | 151 | 2.44 | 69.1 | 0.1 | 6.1 | 2.35 | 67.4 | 0.21 | 19.5 | 2.28 | 66 | 0.13 | 9.1 | 2.13 | 62.8 | 0.19 | 16.6 | 1.97 | 59.7 | 0.09 | 4.3
| 7.- nominal flow | 240 | 3.71 | 63.6 | 0.18 | 12.7 | 3.63 | 62.6 | 0.3 | 41.6 | 3.49 | 61.1 | 0.21 | 19.2 | 3.27 | 58.5 | 0.29 | 35.3 | 2.98 | 55 | 0.13 | 8.9
- connection dimension male thread 3/4"
- NR1-025-ECV1ER... (enthalpy recovery exchanger) -continued Tab.13
Temperature gradient |  |  | 65/50 |  |  |  | 55/45 |  |  |  | 45/35 |  |  |  | 40/30
Inlet air temperature | Degree of air output | Air flow | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop | Heating power of a heater | Exhaust air temperature | Water flow | Water pressure drop
°C | - | m3/hr | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa | kW | °C | m3/hr | kPa
10 | 1.- min/heating mode | 62 | 1.32 | 60.2 | 0.08 | 3.6 | 0.85 | 51.9 | 0.07 | 3.5 | 0.84 | 41.7 | 0.07 | 3.5 | 0.7 | 36.7 | 0.06 | 2.7
| 4. | 151 | 2.26 | 55.7 | 0.13 | 9.2 | 1.44 | 49 | 0.13 | 8.8 | 1.42 | 38.9 | 0.12 | 9 | 1.2 | 34.2 | 0.1 | 6.7
| 7.- nominal flow | 240 | 3.45 | 50.8 | 0.2 | 19.4 | 2.2 | 45.9 | 0.19 | 18.5 | 2.17 | 35.7 | 0.19 | 18.8 | 1.81 | 31.5 | 0.16 | 14
15 | 1.- min/heating mode | 62 | 1.2 | 60.3 | 0.07 | 3 | 0.97 | 51.7 | 0.08 | 4.4 | 0.71 | 41.8 | 0.06 | 2.6 | 0.57 | 36.7 | 0.05 | 1.9
| 4. | 151 | 2 | 56.2 | 0.12 | 7.7 | 1.66 | 48.6 | 0.15 | 11.3 | 1.2 | 39.3 | 0.1 | 6.7 | 0.97 | 34.6 | 0.08 | 4.7
| 7.- nominal flow | 240 | 3.1 | 51.7 | 0.18 | 16.2 | 2.54 | 45 | 0.22 | 23.9 | 1.83 | 36.6 | 0.16 | 13.9 | 1.46 | 32.3 | 0.13 | 9.6
20 | 1.- min/heating mode | 62 | 1.07 | 60.5 | 0.06 | 2.5 | 1.1 | 51.5 | 0.1 | 5.5 | 0.58 | 41.8 | 0.05 | 1.9 | 0.44 | 36.5 | 0.04 | 1.2
| 4. | 151 | 1.82 | 56.7 | 0.11 | 6.3 | 1.88 | 48 | 0.16 | 14 | 0.98 | 39.7 | 0.09 | 4.7 | 0.74 | 34.8 | 0.06 | 2.9
| 7.- nominal flow | 240 | 2.77 | 52.6 | 0.16 | 13.2 | 2.88 | 44.1 | 0.25 | 29.7 | 1.48 | 37.4 | 0.13 | 9.6 | 1.11 | 33 | 0.1 | 5.9
- connection dimension male thread 3/4"

## efficiency - Nroom 100 -Tab.14
Line |  | Nroom-100-efficiency of heat and humidity recovery
Unit type |  | NR1-010-ECxxHR… |  |  |  | NR1-010-ECxxER…
Recovery exchanger type |  | HRV |  |  |  | ERV
|  | AIRFLOW (m3/h) | Temperature % efficiency (EN308) | Current (A) | Power supply (W) | AIRFLOW (m3/h) | Temperature % efficiency (EN308) | Humidity efficiency % (EN308) | Current (A) | Power supply (W)
Degree of air output | 1. | 28 | 94.3 | 0.13 | 10 | 25 | 90 | 85 | 0.13 | 10
| 2. | 41 | 92.4 | 0.14 | 11 | 35 | 87 | 81 | 0.14 | 11
| 3. | 53 | 90.8 | 0.15 | 14 | 47 | 84 | 75 | 0.15 | 14
| 4. | 66 | 89 | 0.18 | 17 | 58 | 81 | 69 | 0.18 | 17
| 5. | 78 | 87.3 | 0.21 | 21 | 69 | 78 | 63 | 0.21 | 21
| 6. | 90 | 85.6 | 0.26 | 26 | 80 | 76 | 58 | 0.26 | 26
| 7. - nominal | 100 | 84.3 | 0.3 | 30 | 90 | 74 | 55 | 0.3 | 30
| 8. BOOST* | 250 | N/A | 1.32 | 167 | 205 | N/A | N/A | 1.32 | 167
* BOOST mode - intensive ventilation

## efficiency - Nroom 250 - Tab.15
Line |  | Nroom-250-efficiency of heat and humidity recovery
Unit type |  | NR1-025-ECxxHR… |  |  |  | NR1-025-ECxxER…
Recovery exchanger type |  | HRV |  |  |  | ERV
|  | AIRFLOW (m3/h) | Temperature % efficiency (EN308) | Current (A) | Power supply (W) | AIRFLOW (m3/h) | Temperature % efficiency (EN308) | Humidity efficiency % (EN308) | Current (A) | Power supply (W)
Degree of air output | 1. | 64 | 94.1 | 0.17 | 13.5 | 62 | 85 | 73 | 0.17 | 13.5
| 2. | 95 | 93 | 0.199 | 17 | 91.6 | 82.5 | 70 | 0.199 | 17
| 3. | 126 | 92 | 0.253 | 23 | 121.2 | 81 | 67 | 0.253 | 23
| 4. | 157 | 91 | 0.319 | 30 | 150.8 | 79.5 | 64 | 0.319 | 30
| 5. | 188 | 90 | 0.45 | 40 | 180.4 | 78 | 60.5 | 0.45 | 40
| 6. | 219 | 89 | 0.52 | 51 | 210 | 76.5 | 58 | 0.52 | 51
| 7. - nominal | 250 | 88.5 | 0.61 | 61 | 240 | 75 | 54.5 | 0.61 | 61
| 8. BOOST* | 350 | N/A | 1.42 | 169 | 335 | N/A | N/A | 1.42 | 169
* BOOST mode - intensive ventilation

## Protection table - Tab.16
Unit type |  | Circuit breaker capacity | Number of phases x voltage
Xroom 100 | NR1-010-ECS0… | 10 | 1x230V
NR1-010-ECV1…
NR1-010-ECE1…
Xroom 250 | NR1-025-ECS0 | 10
NR1-025-ECV1
| NR1-025-ECE1 | 16

## Troubleshooting - Tab.21
- error messages - troubleshooting
Error No. | Error, fault message |  | Possible cause of failure | Troubleshooting
1. | The unit does not start |  | The power cable is not connected | - check the mains connection - check the activation of the safety element
|  |  | The main switch is in position 0 | - set the switch to position I
|  |  | Hold down button 2 (ON/OFF) for a short time, approx. 3 sec | - hold down button 2 (ON/OFF) until the LED above button 2 lights up
| The unit does not start when first commissioned - LED above button 2 is lit |  | The demand for ventilation and heating is switched off | - enter the unit setting mode and check the setting of the ventilation performance requirement and the required temperature (only in the version with electric heating) - make the adjustment according to Section 5.4.2. Tab. 17.
|  |  | Loosened M6x20 bolts with plastic head position 23 of the front metal cover | - securely tighten the bolts on the front metal cover with your hand, Section 3.2.11.
3. | Red indicator light above the FILTER sign is flashing |  | Filter clogging indication | - replace the filter according to Section 6.
4. | No or low ventilation output even when the unit is set to the maximum power |  | Clogged filter | - replace the filter according to Section 6.
|  |  | Contaminated - blocked piping, unit outlets | - Check and clean the unit according to Section 7.
5. | Unit started to be too noisy |  | Clogged filter | - replace the filter according to Section 6.
|  |  | Defective motor bearing | - contact the unit supplier
6. | Electrical heating of the unit does not heat |  | Clogged filter - no flow | - replace the filter according to Section 6.
|  |  | Contaminated - blocked piping, unit outlets | - Check and clean the unit according to Section 7.
|  |  | activated heat exchanger protection against overheating | - switch off the unit with the main switch. Turn the unit on again after 5 minutes (reset of protection). If the problem persists, contact the unit supplier
7. | The night cooling function cannot be switched on (button 6.) - the button signalling flashes 3 times and the function does not switch on |  | Function start conditions are not met - outdoor temperature is too low, heating requirement is too high | - wait for the outside temperature to rise. The function is active only at summer temperatures.
- for XR1-xxx-ECE1... reduce the temperature requirement according to Section 5.4.2. Tab.17 - for XR1-xxx-ECV1... the room air temperature exceeded 35 ° C - the function cannot be used
8. | The night cooling function cannot be switched on (button 6.) - all the status diodes flash once (at buttons 6, 4, 7, 10), the function does not switch on |  | BOOST function active | - switch off the BOOST functions according to Section 5.4.2. Tab.17
|  |  | Active child lock function | - switch off the child lock function according to Section 5.4.2. Tab.17
9. | The BOOST mode cannot be switched on - status diodes flash once or 3 times (at buttons 6, 4, 7, 10), the function does not switch on |  | 3 flashes - very low outdoor temperature | - wait for the outdoor temperature to rise
|  |  | 1 flash - child lock function is active | - switch off the child lock function according to Section 5.4.2. Tab.17
10. | The automatic mode cannot be started - when the button 4 is pressed, the indicator flashes 3 times or lights |  | 3 flashes - unit is not fitted with any AQS sensor | - You probably bought the unit without the AQS sensors or the external sensor is not connected
|  |  | It is still flashing - the sensor connected to the unit is faulty | - if you do not have an external Radon sensor connected to the unit, contact the unit supplier - switch to manual mode according to Section 5.4.2. Tab.17
- if you have an external radon sensor connected to the unit - contact the external sensor supplier - switch to manual mode according to Section 5.4.2. Tab.17
11. | When any button is pressed, the status diodes flash once (at buttons 6, 4, 7, 10) |  | Active child lock function | - switch off the child lock function according to Section 5.4.2. Tab.17
12. | The unit is inoperable and the 4 LEDs on the range for adjusting the ventilation power on the control panel are continuously flashing | - diodes 1; 2; 3; 4 are flashing | Supply fan failure | - turn off the unit on the controller, then by the unit's main switch to position 18, leave the unit off for approx. 10 sec - restart of the unit - if the error persists even after restarting the unit, contact the unit supplier, contact the unit supplier after restarting the unit
13. |  | - diodes 5; 6; 7; 8 are flashing | Exhaust fan failure
14. |  | - diodes 1; 2; 7; 8 are flashing | Faulty "room temperature sensor"
15. |  | - diodes 3; 4; 5; 6 are flashing | Faulty anti-freeze sensor

## controls description Tab.17
- description of buttons
Control description number | Symbol | Button/ Indication | Button description | Active in mode / number of clicks |  |  | Function | Note
|  |  |  | Dormant | Control | Settings
|  |  |  | 0x | 1x | 2x
1. |  | Button | Reduction of ventilation and temperature performance |  |  |  | - Switches from the control mode to ventilation and temperature setting mode - Press the button to reduce the required level by one degree on the range of ventilation power or temperature setting | - Switching between setting the range of the ventilation power or required temperature is done using button 2.
2. |  | Toggle and status indication button | Unit switching on (signalling)/switching off |  |  |  | - By holding the button for 3 seconds, switch the unit on (LED lights up) or off - if the LED flashes after the unit is switched off, the heating is cooled down. Once finished, it will turn off | - in the cold and water versions, the display button has only the on/off function
|  |  | Switching between ventilation power and temperature setting |  |  |  | - In setting mode, you switch between the fan setting and temperature ranges. Indication of the selected range is displayed by flashing of symbols 7 and 10. | - Switching is only for the electric version (NR1-xxx-ECE1...)
3. |  | Toggle function button | Start of intensive ventilation - BOOST |  |  |  | - Pressing the button for 3 seconds starts the intensive 10-minute ventilation. To switch it off before 10 minutes pass, press the button again for 3 seconds and the ventilation returns to the pre-start mode. | - The function start indication is a flashing diode 12.
|  |  | Increase ventilation and temperature power levels |  |  |  | - Switches from the control mode to ventilation and temperature setting mode - Press the button to increase the requirement on the range of the ventilation or temperature performance setting | - switch between the ranges using button 2.
4. |  | Status indication button | Switching between automatic mode (signalling) and manual mode |  |  |  | - By pressing the button, switch to the manual mode, the requirement for permanent ventilation - ventilation is operated upon request of the user, requirements of the AQS sensors are ignored - Press again to activate automatic mode, ventilation as needed - ventilation is operated according to the AQS sensor requirements | - Factory setting is operation in the automatic mode. Diode is lit - When the unit is switched on, the LED diode next to the button is temporarily flashing - sensor calibration
5. |  | Status indication | Filter clogged indication |  |  |  | - The clogged filter indication is triggered after approx. 6 months of unit operation (only if the unit is ventilating). - The indication is expressed by a flashing red LED. | - Replace and reset the filter according to Section 6.
6. |  | Double-function and status indication button | Night cooling - on (signalling)/off |  |  |  | - Press the button to start the night cooling function. Night cooling is used to cool the ventilated area in the summer with night cold air. The function is active for 8 hours from pressing the button. - The intensity of the supplied air can be changed even when the function is activated. When the function is completed, the values return to the settings before the function started. | - It is recommended to activate the function after 10 p.m. During the summer months, the air is coldest around 5 a.m.
|  |  | Child lock |  |  |  | - protection against manipulation by unauthorised persons. It is activated/deactivated by pressing the button for more than 6 sec. Activation/deactivation is indicated by 3 flashes of all the status LEDs | - When attempting to change the parameters during the activated function, all the status LEDs flash once
7. |  | Status indication | Electric heating operation status diode |  |  |  | - in the control mode, the diode is lit - the heating is on - in the setting mode, the diode flashes - you are in the desired temperature setting mode - heating can be switched off independently of the ventilation. In the setting mode, lower the temperature (button 1) until the last diode on the range turns off | – When heating is switched off (all the range diodes are off), all the ventilation functions remain operational.
10. |  | Status indication | Ventilation operation status diode |  |  |  | - in the control mode, the diode is lit - the unit is ventilating - in the setting mode, the diode flashes - you are in the required ventilation power setting mode - ventilation can be switched off independently of the heating requirement. In the setting mode, reduce the output (button 1) until the last diode on the range turns off. | - When ventilation is switched off (all the range diodes are off), all the heating requirements remain operational and satisfied.

## ventilation range - Tab.18
- ventilation range indication display
Control description number | Symbol | Display description | Note
11. |  | Indication of 7 ventilation levels. The LEDs are switched on and off gradually, as required by the user | The setting values are provided in Tab.19.
12. |  | Indication by flashing LED diode - intensive ventilation function activated | If the intensive ventilation function is activated, the entire range for setting the ventilation level is also lit.

## ventilation range - Tab.19
- Assignment of the individual LEDs to the air flow
| Displayed LED on the controller range | NR1-010-ECxxHR… | NR1-010-ECxxER… | Usage examples | NR1-025-ECxxHR… | NR1-025-ECxxER… | Usage examples
|  | m3/h | m3/h |  | m3/h | m3/h
| 1. | 28.4286 | 24.8571 | 1 person - rest mode, sleeping | 64 | 62 | 2 - 3 persons - office activities, sleeping
| 2. | 41 | 35.3714 | 2 persons - rest mode, sleeping | 95 | 91.6 | 3 - 4 persons - office activities, sleeping
| 3. | 53 | 47 | 2 persons - rest mode, sleeping | 126 | 121.2 | 4 - 5 persons – office activities, sleeping; 2 - 3 persons active
| 4. | 65.5 | 58 | 3 persons - rest mode, office | 157 | 150.8 | 6 - 7 persons – office activities, 3 - 4 persons active
| 5. | 78 | 69.2 | 3 - 4 persons - rest mode, office | 188 | 180.4 | 7 - 8 persons – office activities, 4 - 5 persons active
| 6. | 89.8 | 79.6 | 4 persons – office activities | 219 | 210 | 8 - 9 persons – office activities, 5 - 6 persons active
| 7. | 101 | 90 | 4 - 5 persons - office activities | 250 | 240 | 10 persons - office activities, 6 - 7 persons active
| 8. - BOOST* | 250 | 204 | Intensive ventilation | 350 | 335 | Intensive ventilation
* BOOST mode - intensive ventilation

## heating range - Tab.20
- heating range indication display
Control description number | Symbol | Display description |  |  | Note
8. |  | Indication of temperature setting in the selected range. 1st LED
|  | 1st LED | Flake - anti-freeze temperature | 5 - 7 °C
|  | 2nd to 7th LED | Regular temperature setting | 19 - 24 °C | setting in approx. 0.5 °C increments - LED flashes
9. |  | LED in the separate MAX field - signals the maximum possible temperature requirement (approx. 28 °C)
﻿Note:
The assignment of LEDs to the individual temperatures is only indicative. They cannot under any circumstances be regarded as binding.

## Fig. 36
5.4.7. Display of the LED Indicated Statuses on the Controller
Blue LED range diode - ventilation level - 11; 12
- Lit - shows the selected ventilation level
| Status LED - fan - 10. |  |  | - LED 1; 2; 3; 4 flashing - supply fan failure
| Blue |  |  | - LED 5; 6; 7; 8 flashing - exhaust fan failure
| - lit - fan operation |  |  | - LED 1; 2; 7; 8 flashing - “room temp sensor” failure
| - flashing - in the fan power setting mode |  |  | - LED 3; 4; 5; 6 flashing - “anti-freeze” sensor failure
| Status LED - heating - 7. |  |  | LED blue range diode - temperature levels - 8; 9
| Blue |  |  | - lit - displays the selected temperature
- lit - heater in operation
| - flashing - heating power setting mode |  |  | Blue LED status diode - ON/OFF
- lit - the unit controller - ON
- flashes – cooling mode after switching off the control
| Blue LED status diode - automatic (AQS) |  |  | Blue LED status diode - summer mode - 6.
| / manual (depending on the user) - 4. |  |  | - lit - function activated
| - lit - automatic mode ON (AQS) |  |  | - 3 flashes - the function cannot be activated - poor ambient conditions
- flashing - failure of any AQS
Red LED status diode - filter clogging - 5.
- flashing - indicates filter clogging
|  | Common functions for all the blue status diodes | - 3 flashes for activation and deactivation of the "child lock" function
- 1 flash for indicating that the "child lock” function is active
- 3 flashes when starting the BOOST function - cannot be activated - low outdoor temperature

## Basic parameters-QUICK-INSTAL
- Basic technical parameters - Xroom-100 (XR1-010-ECxxHR...)
| Line |  |  | XR1-010-ECS0...X… |  | XR1-010-ECV1...X… |  | XR1-010-ECE1...X… |  | XR1-010-ECS0...P… |  | XR1-010-ECV1...P… |  | XR1-010-ECE1...P…
| Type of recuperation exchanger |  |  | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV
| Unit equipment | pre-heating |  | - |  | - |  | - |  | electric |  | electric |  | electric
|  | final heating |  | - |  | water |  | electric |  | - |  | water |  | electric
| Nominal air output / BOOST* |  | m3/hr | 100/250 | 90/205 | 100/250 | 90/205 | 100/250 | 90/205 | 100/250 | 90/205 | 100/250 | 90/205 | 100/250 | 90/205
| Heat output (range) of heating** |  | kW | - |  | 0.33 - 1.38 | 0.29 - 1.24 | 0.5 |  | - |  | 0.33 - 1.38 | 0.29 - 1.24 | 0.5
| Noise level** |  | dB(A) | 32.1
| Weight**** |  | kg | 16.3 |  | 18.3 |  | 19.3 |  | 16.8 |  | 18.8 |  | 19.8
| Water volume in boiler |  | l | - |  | 0.51 |  | - |  | - |  | 0.51 |  | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of unit / BOOST* |  | W | 30/167 |  | 30/167 |  | 530/667 |  | 300/437 |  | 300/437 |  | 800/937
| Nominal current of the unit / BOOST* |  | A | 0.3/1.32 |  | 0.3/1.32 |  | 2.5/3.5 |  | 1.5/2.5 |  | 1.5/2.5 |  | 3.7/4.7
| Recovery efficiency per EN 308 | heat | % | up to 87 | up to 90 | up to 87 | up to 90 | up to 87 | up to 90 | up to 87 | up to 90 | up to 87 | up to 90 | up to 87 | up to 90
|  | humidity | % | - | up to 85 | - | up to 85 | - | up to 85 | - | up to 85 | - | up to 85 | - | up to 85
| Protection type |  | IP | 20
| Energy efficiency ratio (ERP) |  |  | cold climate A+ (-47 HRV, -45.9 ERV); medium climate A (-40,4 HRV, -38.9 ERV); warm climate A (-34.1 HRV), warm climate B (-33.1 ERV)
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging
- Basic technical parameters - Nroom-250 (NR1-025-ECxxHR...)
| Line |  |  | NR1-025-ECS0...X… |  | NR1-025-ECV1...X… |  | NR1-025-ECE1...X… |  | NR1-025-ECS0...P… |  | NR1-025-ECV1...P… |  | NR1-025-ECE1...P…
| Type of recuperation exchanger |  |  | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV | HRV | ERV
| Unit equipment | pre-heating |  | - |  | - |  | - |  | electric |  | electric |  | electric
|  | final heating |  | - |  | water |  | electric |  | - |  | water |  | electric
| Nominal air output / BOOST* |  | m3/hr | 250/350 | 240/335 | 250/350 | 240/335 | 250/350 | 240/335 | 250/350 | 240/335 | 250/350 | 240/335 | 250/350 | 240/335
| Heat output (range) of heating** |  | kW | - |  | 1.34 - 3.49 |  | 1 |  | - |  | 1.34 - 3.49 |  | 1
| Noise level** |  | dB(A) | 32.6
| Weight**** |  | kg | 36 |  | 39.4 |  | 41.2 |  | 37 | 21.281 | 40.4 | 21.7524 | 42.2
| Water volume in boiler |  | l | - |  | 1.17 |  | - |  | - |  | 1.17 |  | -
| Power supply of the unit |  | V/Hz | 1 ~ 230 / 50-60
| Nominal input power of unit / BOOST* |  | W | 61/169 |  | 61/169 |  | 1061/1169 |  | 479/709 |  | 479/709 |  | 1480/1709
| Nominal current of the unit / BOOST* |  | A | 0.61/1.42 |  | 0.61/1.42 |  | 5/5.8 |  | 3/3.8 |  | 3/3.8 |  | 7.3/8.2
| Recovery efficiency per EN 308 | heat | % | up to 87 | up to 86 | up to 87 | up to 86 | up to 87 | up to 86 | up to 87 | up to 86 | up to 87 | up to 86 | up to 87 | up to 86
|  | humidity | % | - | up to 75 | - | up to 75 | - | up to 75 | - | up to 75 | - | up to 75 | - | up to 75
| Protection type |  | IP | 20
| Energy efficiency ratio (ERP) |  |  | cold climate A+ (-47.5 HRV, -47.2 ERV); medium climate A (-40.5 HRV, -40.2 ERV); warm climate A (-34,6 HRV, -34,4)
* BOOST mode - intensive ventilation
** at the temperature gradient of 75/60 and an inlet air temperature of 20 °C
*** Sound pressure level in free space at a distance of 3 m
**** unit weight, without water and packaging

## EPS BOX-tab
Installation EPS box
| Type of installation EPS box ordering code | Thermal conductivity coefficient λ | thermal resistance RD | approximate bulk density | compressive stress at 10% compression | fire reaction class | net/gross weight | packaging dimensions
|  | W/m.K | m2.K/W | kg/m3 | kPa | - | kg | m (H x W x L)/pc*
| NR-010-EPS-BOX | 0.037 | 5.4 | 18 - 23 | 100 | E | 0.9/1 | 0.45 x 0.2 x 0.5/32
| NR-025-EPS-BOX | [5 empty] | 1.1/1.2 | 0.54 x 0.2 x 0.5/32
*Number of pieces on the pallet